## Slide 1: Haystack Labs WG Update: Portfolio & Attributes
Track 2 – Session 2
Annie Dehghani
Buildings IOT

## Slide 2: Overview
2 New Concepts Introduced to Haystack:
  Portfolio
  Attributes

## Slide 3: Portfolios
Higher Level organization and grouping for sites

## Slide 4: portfolio, portfolioRef
def: ^portfolio
is: ^entity
doc: "A collection of sites“
def: ^portfolioRef
is: ^ref
of: ^portfolio
tagOn: [^site, portfolio]
containedBy: ^portfolio
site
portfolio
portfolio
portfolio
site
portfolioRef

## Slide 5: campus
def: ^campus
is: ^site
doc: "A collection of contiguous sites. “
site
campus
site
siteRef
site

## Slide 6: building
def: ^building
is: ^site
doc: "A closed structure with walls and a roof."
usage: building site

## Slide 7: Attributes
Static (not time-series) meta data about an entity, typically an equip
Examples include: equipment schedules and name plate data, BIM data

## Slide 8: Typical Attributes
Identifying Information
  Make
  Model
  Serial number
Equipment size
  Capacity
  Airflow
  Power
  Voltage
Spatial Attributes
  Gross Floor Area
  Design Occupancy

## Slide 9: Modelling Considerations
Attributes have a scalar value
Attributes are messy just like points
  Model as a "bag" of marker tags on an equip ?
    Camel case is fraught: heatEnergyMaxRatedOutput or is it maxHeatEnergyRatedOutput?
  Model each attribute as a Dict with the val tag?
    Soo many attribute records
{heat energy max output rated val:425kBTU id: @heatEnergyAttr1}
{heat energy max input rated val:525kBTU @heatEnergyAttr2}

## Slide 10: Question at Hand
How to associate attribute Dicts with a given entity (equip most common use case)
There could be lots of them (potentially many more than points) – do we want each one to be a first class entity with its own id?
Most name plate attributes are shared between equipment models
Avoid needlessly bringing back a huge list of attributes every time an entity is queried

## Slide 11: Attributes Model
id:@ahu
attrsRef: @ahu-attrs
id: @ahu-attrs
attrs: [
{modelNum val:"48A3T025DNV62AHP"}
{serialNum val:"0517U4481"}
{heat energy max output rated val:425kBTU},
{heat energy max input rated val:525kBTU},
]
equip
attrsRef
attrs

## Slide 12: List of Attributes Refs
id:@ahu-1
attrsRef:[@ahu-1-attrs, @fan-attrs , @coil-attrs ]
id:@ahu-1-attrs
attrs: [
{serialNum val:"0517U4481"}
]
id:@fan-attrs
attrs: [
{fan rated power energy max output rated val:5hp},
{fan design static pressure val:1.5”w.g. },
]
id:@coil-attrs
attrs: [
{coil design flow rate val:10gpm},
{coil design water pressure delta val:10ft H20},
]
equip
attrs
attrs
attrs
attrsRef

## Slide 13: Attributes Nested Directly on Equip
id:@ahu
attrsRef: @ahu
attrs: [
{modelNum val:"48A3T025DNV62AHP"}
{serialNum val:"0517U4481"}
{heat energy max output rated val:425kBTU},
{heat energy max input rated val:525kBTU},
]
attrsRef
attrs
equip

## Slide 14: Questions?

## Slide 15: Querying
Current filter syntax is not going to handle looking up a specific attribute Dict
Do we need to? We could just leave it up to implementations to implement an attrs() function
We also could potentially handle via Xeto query slots which work more like GraphQL

## Slide 16: Xeto
We could solve attributes more elegantly using native Xeto
IMO better to solve modeling strictly with existing Haystack data structures
Leverage Xeto for templates and validation
Attribute template/validation very similar to point templates