## Slide 1: Data Modeling for Electrical Systems
Technical Track
Rick Jennings, PE, CEM

## Slide 2: Agenda
Update on Xeto electrical point specs
Power quality monitoring applications
Community examples
Smart building & EV charging interface
Next steps & wrap up

## Slide 3: Xeto Electrical Point Specs
Technical Track

## Slide 4: Data Specifications for RFPs and Beyond
Example Specification for a Net Energy Meter
Xeto Library | Spec Name | Description
ph.points | ElecAcTotalNetActiveEnergySensor | Sensor for total net of AC electric active energy
ph.points.elec | ElecAcTotalNetActivePowerSensor | Sensor for total net of average magnitude of AC electric active power
Benefits:
Precision
Streamlined
Consistency
Xeto specs are intended to augment vendor documentation.
Xeto specs can be referenced in RFPs like this using data available from the specs themselves.

## Slide 5: Example: Composing Elec Point Specs
Applies active for the required ElecAcPowerSubtype choice
Applies import for the required ElecDirection choice
ElecSensor
ElecDemandSensor
ElecAcDemandSensor
ElecAcActiveDemandSensor
ElecAcImportActiveDemandSensor
ElecAcTotalImportActiveDemandSensor
Applies total for elec location
ElecAc prefix
Sensor suffix
Add tags to the left

## Slide 6: Xeto Libraries for Elec Point Specs
ph.points library
AC demand & energy sensors
Total location only
ph.points.elec library
AC power, voltage, current, & power factor sensors
Other locations for AC demand & energy
DC specs
Elec setpoint specs
Library placement of specs are subject to change.

## Slide 7: Spec Count Across Elec Point Libraries
These counts are subject to change.
 | ph.points | ph.points.elec | Both Libraries
Abstract Spec Count | 29 | 46 | 75
Concrete Spec Count | 26 | 156 | 182
Total Spec Count | 55 | 202 | 257
Previously was 579
(~56% reduction)

## Slide 8: Power Quality Monitoring Applications
Technical Track

## Slide 9: Motivation for Power Quality Analysis
Ideal
Impact of Harmonics
Harmonics can lead to energy waste, suboptimal equipment performance due to transistor misfiring, and premature equipment failure

## Slide 10: Decomposing Electrical Waveforms
Goal is to support semantics for data points offered by power quality meters (e.g., THD or IHD)

## Slide 11: Waveform Capture
Loss of Power
Working towards supporting waveform capture for advanced use cases.

## Slide 12: Modeling Power Quality Metrics
ElecAcWaveformStat: Choice
ElecAcThffWaveformStat: ElecAcWaveformStat { telephoneHarmonicFormFactor }
ElecAcIhdWaveformStat: ElecAcWaveformStat { individualHarmonicDistortion }
ElecAcThdWaveformStat: ElecAcWaveformStat { totalHarmonicDistortion }
ElecAcOddThdWaveformStat: ElecAcWaveformStat { oddTotalHarmonicDistortion }
ElecAcEvenThdWaveformStat: ElecAcWaveformStat { evenTotalHarmonicDistortion }
ElecAcKFactorWaveformStat: ElecAcWaveformStat { kFactor }
ElecAcCrestFactorWaveformStat: ElecAcWaveformStat { crestFactor }
ElecAcImbalanceWaveformStat: ElecAcWaveformStat { imbalance }
ElecAcLineStatCurrentSensor {
totalHarmonicDistortion
lineCurrent: "L1"
}
Example Usage
Plan to convert ElecAcWaveformStat to ElecAcWaveformMetric

## Slide 13: Community Examples
Technical Track

## Slide 14: Community Product Examples
ABB ACH580 VFD
Multi-Circuit Submeter
Advanced Power & Energy Meter
Example Elec Panel
Level 3 DC EVSE
Level 2 AC EVSE

## Slide 15: Example: Accuenergy’s Acuvim 2
Acuvim2ElecMeter : AcElecMeter <abstract> {
attrs: Query {
ManufacturerAttr { val: "Accuenergy" }
ModelSeriesAttr { val: "Acuvim II" }
DimensionLengthAttr { val: 96mm }
DimensionWidthAttr { val: 96mm }
DimensionHeightAttr { val: 64.3mm }
TempRatedMinOperatingAttr { val: -25°C }
TempRatedMaxOperatingAttr { val: 70°C }
}
points: {
ElecAcFreqSensor {
modbusAddr: ModbusAddr { addr: "16384", encoding: "f4" }
bacnetAddr: BacnetAddr { addr: "AI1" }
}
ElecAcPhaseVoltSensor {
phaseVolt: "L1-N"
modbusAddr: ModbusAddr { addr: "16386", encoding: "f4" }
bacnetAddr: BacnetAddr { addr: "AI2" }
}
...
}
}
Attributes
Points

## Slide 16: Modeling Single Line Diagrams using Xeto
Use cases
Capacity management
Service operations
Panel example actively being worked on in the Labs WG

## Slide 17: Smart Building & EV Charging Interface
Technical Track

## Slide 18: Most EV Charging occurs in the Built Environment
Completely new paradigm than refueling petrol vehicles
Opportunities to leverage unused electrical capacity in a building
“The electric-vehicle market in 2030 will require more than 55 million chargers in buildings, consuming at least 525 TWh per year.” (Source: McKinsey & Company)
Mostly Level 2 EV chargers in buildings
Synergies with:
  Residential & Multifamily housing
  Building & Fleet Electrification
  Solar & Battery Energy Storage
  Energy Efficiency

## Slide 19: Smart Building & EV Charging Interface
To Utility
MSB
3-Phase, 480Y/277V
EV Panel
3-Phase, 208Y/120V
ElecAcLineImportCurrentMaxSp { lineCurrent: “L1” }
ElecAcLineImportCurrentMaxSp { lineCurrent: “L2” }
ElecAcLineImportCurrentMaxSp { lineCurrent: “L3” }
3P
3P
Limits scope for the EV charging system integrator and allows for the smart building system integrator to indirectly control EVSE loads
ElecAcTotalImportActiveDemandMaxSp
To Building
Loads

## Slide 20: Next Steps & Wrap Up
Technical Track

## Slide 21: Next Steps
Freeze APIs for ph.points & ph.points.elec ASAP
  Lower-level dependency
  Stay tuned for upcoming draft reviews
  No set deadline yet
Ramp up elec attribute initiative
Iterate on the 6+ xeto-cc electrical product examples
  “benchtesting” initiative

## Slide 22: Wrap Up
Significant progress on Xeto electrical points
Better support for advanced power monitoring applications
Community examples for education and project assistance
Smart building & EV charging interface for happier end customers
Thanks to all contributors!