## Slide 1
Haystack Data Modeling Boiler Controls
April Slotterback and Jakob Bell

## Slide 2: How do we tag every boiler in New York City?
Photo by J. Bohm

## Slide 3: ABOUT US
Company founded 2012
Customer base: NYC metro area
Controls and monitoring for 350+ heating plants (25+ mm sqft)
Service 700+ heating plants
100+ active mechanical installation projects
100+ Employees

## Slide 4
Service, Installation, & Compliance
24 Hour Emergency Service
Boilers, Burners, Water Heaters
Oil to Gas Conversions, CHP
Triennial, BO-9, Backflow Filings.
Real Time Energy Management
Monitor & Control - fault detection, reliability, efficiency
Preventative & Proactive Service
Demand Management & Load Shifting
Energy supply risk management
Maximize Comfort, Minimize Costs, Increase NOI
Integrated Energy Services

## Slide 5: Axxon Architecture
CPT API
Wiring, BACnet, Modbus, et al
Sedona Connector
Inovonics Connector
Haystack
Connector

## Slide 6: Boiler Tagging

## Slide 7: Early Axxon Controls
The boiler is one equip
All points, whether sensors, setpoints, or commands, were under this boiler equip.
Write once, install everywhere.

## Slide 8: Oversimplification
Photo by N. Cruz
“Boiler”
“Boiler 2”

## Slide 9: Increasing Technical Debt
Undocumented features/revisions
Lack of version control for configurations
Rapid expansion of system control offerings
Covid turnover -> loss of institutional memory
Result: Unreliable code that took very long to develop and maintain

## Slide 10: Cleaning Up

## Slide 11: Axxon Controls
CPT API
Wiring, BACnet, Modbus, et al
Sedona Connector
Inovonics Connector
Haystack
Connector

## Slide 12: Wrangling the technical debt: controllers
Listening to customer complaints
Cataloging existing systems
Correcting known bugs in older systems
Result: More consistent controls

## Slide 13: Axxon Data Model
CPT API
Wiring, BACnet, Modbus, et al
Sedona Connector
Inovonics Connector
Haystack
Connector

## Slide 14: Building Better Data Models
  pump number:1
  pump number:2
Photo by N. Cruz
hot water boiler number:1
hot water boiler number:2
flue duct
primaryLoop hot water pipe
secondaryLoop hot water pipe

## Slide 15: Axxon Control Panel
axxon controls panel
heating controls panel
outside air thermostat
indoor air thermostat
primaryLoop reset
secondaryLoop pump sequencer
boiler sequencer
….
domestic hot water controls panel
domestic hot water thermostat
(red tags above are custom tags)

## Slide 16: Axxon Server
CPT API
Wiring, BACnet, Modbus, et al
Sedona Connector
Inovonics Connector
Haystack
Connector

## Slide 17: Cloud Responsibilities

## Slide 18: Custom Tags in Action
setpointsTable
advancedTable
boilerSpecific
systemStatusTable

## Slide 19: Custom Tags in Action
  hwViewPoint
  mobilePoint
  portfolioViewPoint
  heatViewPoint
  heatCallComponent
  chartGroup: Used to sort data and group charts by default

## Slide 20: Challenges with Custom Tags
Hard to maintain
Difficult to create custom views without hacky workarounds
Poor documentation
Unnecessary learning curve for new employees

## Slide 21: Shifting to Templates
New Approach: Replaced custom tags with templates
Templates allow implementers a structured format to define views and charts
Templates eliminate the need for custom tags
Template types include:
  Frontend tile templates
  Chart templates

## Slide 22: Chart Templates

## Slide 23: Frontend View Templates

## Slide 24: Improved Maintainability
Improved Maintainability
  Clear templates replace obscure tags
  Better documentation and standardization
Enhanced Customization
  Templates allow flexible, site-specific views and charts
Scalability
  Easier to adapt to new requirements
  Future-proof with Xeto Specs integration

## Slide 25: Future Plans
Use Xeto specs as a commissioning tool:
  Validate new and existing data models
  Allow structural typing to determine templates
Example Xeto Spec Checking For Templates:

## Slide 26: Conclusion
Don’t optimize too soon
  Early assumptions caused us to have substantial technical dept
Use existing tagging structure as much as possible.
  Custom tags should be used sparingly and be thoroughly documented.
  Views, Rules, and charts should be built using standard tagging whenever possible.
Design with flexibility in mind
  Consider adding new equips, zones, spaces, etc.
  Don’t shove every point into a single equip.

## Slide 27: Thank you

## Slide 28
Dual Fuel Corp.
32 Cortlandt Street
Mount Vernon, NY 10550
347-669-2427
April Slotterback
Software Engineer
aslotterback@dualfuelcorp.com
Jakob Bell
Software Engineer jbell@dualfuelcorp.com
www.dualfuelcorp.com